## DB-EXT
PROJECT: PROPOSED VILLA (B+ G+ 1) | [7 empty] | LOAD DISTRIBUTION SCHEDULE | [20 empty] | LOCATION : UNDER GROUND FLOOR
DB NOS. : DB - GF | [28 empty] | MOUNTING : FLUSH
FED FROM : SMDB -1
RATING OF INCOMER | RATING OF ELCB |  |  |  | MCB | CCT | ECC | LOCATION | CONNECTED LOAD / POINTS | [20 empty] | LOAD PER CIRCUIT WATT |  |  | REMARKS
|  | SEC. | SL. | CIRC | RTG. | WIRE | WIRE
|  | No. | No. | No. | IN | SIZE | SIZE |  | EX-01 | EX-02 | O1 LED | SL | ML | TL | CO | CLOSET LGT | DL | CHL | 13A S/S | 13A D/S | 15A S/S | WASHING /M | MICRO/W | OVEN | COOKER | SHAVER | FCU | ISO | WATT/UNIT | R | Y | B
[5 empty] | AMP | mm2 | mm2
[9 empty] | 10 | 10 | 10 | 15 | 50 | 50 | 10 | 10 | 100 | 200 | 200 | 400 | 1000 | 500 | 1200 | 1200 | 3000 | 200
TPN ISOLATOR 40A | 40A 4P 100mA | 1 | 1 | R1 | 10 | 3CX2.5 |  | COMPOUND WALL | 5 | 5 |  | 2 | [16 empty] | 30 | 130 |  |  | ARMOURED
|  |  | 2 | Y1 | 10 | 3CX2.5 |  | COMPOUND WALL | 9 | [19 empty] | 30 |  | 90 |  | ARMOURED
|  |  | 3 | B1 | 10 | 3CX2.5 |  | COMPOUND WALL | 14 | [19 empty] | 30 |  |  | 140 | ARMOURED
|  |  | 4 | R2 | 10 | 3CX2.5 |  | OUTSIDE |  |  | 37 | [17 empty] | 10 | 370 |  |  | ARMOURED
|  |  | 5 | Y2 | 10 | 3CX2.5 |  | OUTSIDE |  |  | 7 | [17 empty] | 10 |  | 70 |  | ARMOURED
|  |  | 6 | B2 | 10 |  |  | SPACE | [20 empty] | 10 |  |  | 0
| 40A 4P 100mA | 2 | 7 | R3 | 10 | 2.5 | 2.5 | PERGOLA | 3 |  |  | 8 |  |  | 28 | [14 empty] | 430 |  |  | RING
|  |  | 8 | Y3 |  |  |  | SPACE | [22 empty] | 0
|  |  | 9 | B3 |  |  |  | SPACE | [23 empty] | 0 | RING
|  |  | 10 | R4 |  |  |  | SPACE | [21 empty] | 0 |  |  | RING
|  |  | 11 | Y4 |  |  |  | SPACE | [22 empty] | 0
|  |  | 12 | B4 |  |  |  | SPACE | [23 empty] | 0 | RONG
| 40A 4P 30mA | 3 | 13 | R5 | 32 | 4 | 4 | COMPOUND WALL | [10 empty] | 5 | [9 empty] | 200 | 1000 |  |  | RING
|  |  | 14 | Y5 | 20 | 4 | 4 | MOTOR GATE 1 | [19 empty] | 1 | 500 |  | 500 |  | MOTOR GATE 1
|  |  | 15 | B5 | 20 | 4 | 4 | MOTOR GATE 2 | [19 empty] | 1 | 500 |  |  | 500 | MOTOR GATE 2
|  |  | 16 | R6 | 32 | 4 | 4 | PERGOLA | [10 empty] | 4 | [9 empty] | 200 | 800 |  |  | RING
|  |  | 17 | Y6 | 20 | 4 | 4 | PERGOLA | [14 empty] | 1 | [5 empty] | 1200 |  | 1200 |  | MICROWAVE
|  |  | 18 | B6 | 32 | 6 | 6 | PERGOLA | [16 empty] | 1 |  |  |  | 3000 |  |  | 3000 | COOKER
| 40A 4P 30mA |  | 19 | R7 | 20 | 4 | 4 | PERGOLA | [11 empty] | 1 | [9 empty] | 400 |  |  | FLOOR BOX
|  |  | 20 | Y7 | 20 | 4 | 4 | WATER PUMP | [19 empty] | 1 | 1600 |  | 1600 |  | WATER PUMP
|  |  | 21 | B7 |  |  |  | SPACE | [23 empty] | 0
|  |  | 22 | R8 | 32 | 6 | 6 | SUCTION PUMP | [19 empty] | 1 | 4000 | 4000 |  |  | SUCTION PUMP
|  |  | 23 | Y8 | 20 | 4 | 4 | SUB PUMP | [19 empty] | 1 | 1000 |  | 1000 |  | SUB PUMP
|  |  | 24 | B8 |  |  |  | SPACE | [23 empty] | 0
|  |  | 25 | R9 | [25 empty] | 0
|  |  | 26 | Y9 | [26 empty] | 0
|  |  | 27 | B9 | [27 empty] | 0
|  |  | 28 | R10 | [25 empty] | 0
|  |  | 29 | Y10 | [26 empty] | 0
|  |  | 30 | B10 | [27 empty] | 0
|  |  | 31 | R11 | [25 empty] | 0
|  |  | 32 | Y11 | [26 empty] | 0
|  |  | 33 | B11 | [27 empty] | 0
|  |  | 34 | R12 | [25 empty] | 0
|  |  | 35 | Y12 | [26 empty] | 0
|  |  | 36 | B12 | [27 empty] | 0
|  |  | 37 | R13 | [25 empty] | 0
|  |  | 38 | Y13 | [26 empty] | 0
|  |  | 39 | B13 | [27 empty] | 0
|  |  | 40 | R14 | [25 empty] | 0
|  |  | 41 | Y14 | [26 empty] | 0
|  |  | 42 | B14 | [27 empty] | 0
|  |  | 43 | R15 | [25 empty] | 0
|  |  | 44 | Y15 | [26 empty] | 0
|  |  | 45 | B15 | [27 empty] | 0
|  |  | 46 | R16 | [25 empty] | 0
|  |  | 47 | Y16 | [26 empty] | 0
|  |  | 48 | B16 | [27 empty] | 0
[29 empty] | TOTAL | 7130 | 4460 | 3640
[30 empty] | 7.13 | 4.46 | 3.64
[29 empty] | TOTAL CONNECTED LOAD IN kW |  |  |  | 15.23
CABLE SIZE : 4C x 10mm2 Cu./XLPE /SWA/PVC + 1C x 10mm2 CU/PVC/ Y-G ECC. | [8 empty] | LTG = Lighting,F/O = Flex Outlet for display unit, ISO = Isolator, FCU = Fan Coil Unit
FCU = Fan Coil Unit, W/H.=Water Heater, SS/O= Socket/Outlet, DS/O = Double socket/Outlet

## DB-UGF-L
PROJECT: PROPOSED VILLA (B+ G+ 1) | [7 empty] | LOAD DISTRIBUTION SCHEDULE | [21 empty] | LOCATION : UNDER GROUND FLOOR
DB NOS. : DB - UGF-L | [29 empty] | MOUNTING : FLUSH
FED FROM : SMDB -1 | [29 empty] | AREA |  |  | PLOT NO
RATING OF INCOMER | RATING OF ELCB |  |  |  | MCB | CCT | ECC | LOCATION | CONNECTED LOAD / POINTS | [21 empty] | LOAD PER CIRCUIT WATT |  |  | REMARKS
|  | SEC. | SL. | CIRC | RTG. | WIRE | WIRE
|  | No. | No. | No. | IN | SIZE | SIZE |  | EX-01 | EX-02 | O1 LED | SL | ML | TL | CO | CLOSET LGT | DL | CHL | 13A S/S | 13A D/S | 15A S/S | WASHING /M | DISH WASHER | MICRO/W | OVEN | COOKER | SHAVER | FCU | ISO | WATT/UNIT | R | Y | B
[5 empty] | AMP | mm2 | mm2
[9 empty] | 10 | 10 | 10 | 15 | 50 | 50 | 10 | 10 | 100 | 200 | 200 | 400 | 1000 | 500 | 500 | 1200 | 1200 | 3000 | 200
TPN ISOLATOR 40A | 40A 4P 100mA | 1 | 1 | R1 | 10 | 2.5 | 2.5 | DRIVER ROOM |  |  |  | 7 | 1 | [17 empty] | 155
|  |  | 2 | Y1 | 10 | 2.5 | 2.5 | ELECTRIC ROOM & PUMP ROOM | [5 empty] | 4 | [17 empty] | 200
|  |  | 3 | B1 | 10 | 2.5 | 2.5 | MAIDROOM( 1&2 ) & LOUNDRY + WC + BATH+PATIO | 2 |  |  | 24 | 1 | [19 empty] | 430
|  |  | 4 | R2 | 10 | 2.5 | 2.5 | PARKING | [5 empty] | 38 | [16 empty] | 1900
|  |  | 5 | Y2 | 10 | 2.5 | 2.5 | BEAUTY ROOM |  |  |  | 6 | 1 | [18 empty] | 140
|  |  | 6 | B2 | 10 | 2.5 | 2.5 | STAIRS |  |  | 20 | [21 empty] | 200
| 40A 4P 100mA | 2 | 7 | R3 | 10 | 2.5 | 2.5 | ENTRANCE LOBBY |  |  | 4 | 8 | 1 |  | 16 | [15 empty] | 370
|  |  | 8 | Y3 | 10 | 2.5 | 2.5 | CINEMA ROOM |  |  |  | 12 |  |  | 24 | [16 empty] | 420
|  |  | 9 | B3 | 10 | 2.5 | 2.5 | TRADITIONAL AREA |  |  |  | 32 | [20 empty] | 480
|  |  | 10 | R4 | 10 | 2.5 | 2.5 | ENTRANCE LOBBY | [9 empty] | 1 | [12 empty] | 200
|  |  | 11 | Y4 | 10 | 2.5 | 2.5 | STORE | [5 empty] | 10 | [17 empty] | 500
|  |  | 12 | B4 | 10 | 2.5 | 2.5 | GAME ROOM |  |  |  | 36 |  |  | 48 | [17 empty] | 1020
| 40A 4P 100mA | 3 | 13 | R5 | 10 | 2.5 | 2.5 | STAIRS + PATIO + LOCKER |  |  |  | 18 |  | 2 | [16 empty] | 370
|  |  | 14 | Y5 |  |  |  | SPACE | [23 empty] | 0
|  |  | 15 | B5 |  |  |  | SPACE | [24 empty] | 0
|  |  | 16 | R6 |  |  |  | SPACE | [22 empty] | 0
|  |  | 17 | Y6 |  |  |  | SPACE | [23 empty] | 0
|  |  | 18 | B6 | 20 | 4 | 4 | TRADITIONAL AREA | [19 empty] | 1 |  | 200 |  |  | 200 | FCU
| 40A 4P 100mA | 4 | 19 | R7 | 20 | 4 | 4 | BEAUTY ROOM | [19 empty] | 1 |  | 200 | 200 |  |  | FCU
|  |  | 20 | Y7 | 20 | 4 | 4 | CINEMA ROOM | [19 empty] | 1 |  | 200 |  | 200 |  | FCU
|  |  | 21 | B7 | 32 | 4 | 4 | MAID ROOM 1& 2 | [19 empty] | 1 |  | 200 |  |  | 200 | FCU
|  |  | 22 | R8 | 20 | 4 | 4 | STORE | [19 empty] | 1 |  | 200 | 200 |  |  | FCU
|  |  | 23 | Y8 | 20 | 4 | 4 | GAME ROOM | [19 empty] | 1 |  | 200 |  | 200 |  | FCU
|  |  | 24 | B8 | 20 | 4 | 4 | GAME ROOM | [19 empty] | 1 |  | 200 |  |  | 200 | FCU
|  |  | 25 | R9 | [26 empty] | 0
|  |  | 26 | Y9 | [27 empty] | 0
|  |  | 27 | B9 | [28 empty] | 0
|  |  | 28 | R10 | [26 empty] | 0
|  |  | 29 | Y10 | [27 empty] | 0
|  |  | 30 | B10 | [28 empty] | 0
|  |  | 31 | R11 | [26 empty] | 0
|  |  | 32 | Y11 | [27 empty] | 0
|  |  | 33 | B11 | [28 empty] | 0
|  |  | 34 | R12 | [26 empty] | 0
|  |  | 35 | Y12 | [27 empty] | 0
|  |  | 36 | B12 | [28 empty] | 0
|  |  | 37 | R13 | [26 empty] | 0
|  |  | 38 | Y13 | [27 empty] | 0
|  |  | 39 | B13 | [28 empty] | 0
|  |  | 40 | R14 | [26 empty] | 0
|  |  | 41 | Y14 | [27 empty] | 0
|  |  | 42 | B14 | [28 empty] | 0
|  |  | 43 | R15 | [26 empty] | 0
|  |  | 44 | Y15 | [27 empty] | 0
|  |  | 45 | B15 | [28 empty] | 0
|  |  | 46 | R16 | [26 empty] | 0
|  |  | 47 | Y16 | [27 empty] | 0
|  |  | 48 | B16 | [28 empty] | 0
[30 empty] | TOTAL | 3395 | 1660 | 2730
[31 empty] | 3.395 | 1.66 | 2.73
[30 empty] | TOTAL CONNECTED LOAD IN kW |  |  |  | 7.785
CABLE SIZE : 4C x 10mm2 Cu./XLPE /SWA/PVC + 1C x 10mm2 CU/PVC/ Y-G ECC. | [8 empty] | LTG = Lighting,F/O = Flex Outlet for display unit, ISO = Isolator, FCU = Fan Coil Unit
FCU = Fan Coil Unit, W/H.=Water Heater, SS/O= Socket/Outlet, DS/O = Double socket/Outlet

## DB-UGF-P
PROJECT: PROPOSED VILLA (B+ G+ 1) | [7 empty] | LOAD DISTRIBUTION SCHEDULE | [21 empty] | LOCATION : UNDER GROUND FLOOR
DB NOS. : DB - UGF-P | [29 empty] | MOUNTING : FLUSH
FED FROM : SMDB -1 | [29 empty] | AREA |  |  | PLOT NO
RATING OF INCOMER | RATING OF ELCB |  |  |  | MCB | CCT | ECC | LOCATION | CONNECTED LOAD / POINTS | [21 empty] | LOAD PER CIRCUIT WATT |  |  | REMARKS
|  | SEC. | SL. | CIRC | RTG. | WIRE | WIRE
|  | No. | No. | No. | IN | SIZE | SIZE |  | EX-01 | EX-02 | O1 LED | SL | ML | TL | CO | CLOSET LGT | DL | CHL | 13A S/S | 13A D/S | 15A S/S | WASHING /M | DISH WASHER | MICRO/W | OVEN | COOKER | SHAVER | FCU | ISO | WATT/UNIT | R | Y | B
[5 empty] | AMP | mm2 | mm2
[9 empty] | 10 | 10 | 10 | 15 | 50 | 50 | 10 | 10 | 100 | 200 | 200 | 400 | 1000 | 500 | 500 | 1200 | 1200 | 3000 | 200
TPN ISOLATOR 63A | 40A 4P 100mA | 1 | 1 | R1 | [26 empty] | 0
|  |  | 2 | Y1 | [27 empty] | 0
|  |  | 3 | B1 | [28 empty] | 0
|  |  | 4 | R2 | [26 empty] | 0
|  |  | 5 | Y2 | [27 empty] | 0
|  |  | 6 | B2 | [28 empty] | 0
| 40A 4P 100mA | 2 | 7 | R3 | [26 empty] | 0
|  |  | 8 | Y3 | [27 empty] | 0
|  |  | 9 | B3 | [28 empty] | 0
|  |  | 10 | R4 | [26 empty] | 0
|  |  | 11 | Y4 | [27 empty] | 0
|  |  | 12 | B4 | [28 empty] | 0
| 40A 4P 100mA | 3 | 13 | R5 | [26 empty] | 0
|  |  | 14 | Y5 | [27 empty] | 0
|  |  | 15 | B5 | [28 empty] | 0
|  |  | 16 | R6 | [26 empty] | 0
|  |  | 17 | Y6 | [27 empty] | 0
|  |  | 18 | B6 | [28 empty] | 0
| 40A 4P 30mA |  | 1 | R1 | 20 | 4 | 4 | DRIVER ROOM | [10 empty] | 3 | [11 empty] | 600
|  |  | 2 | Y1 | 32 | 4 | 4 | ELECTRIC ROOM + MECHANICAL ROOM | [10 empty] | 1 | 2 | [11 empty] | 1000 |  | RING
|  |  | 3 | B1 | 32 | 4 | 4 | MAID ROOM 2 | [10 empty] | 4 | 1 | [12 empty] | 1200 | RING
|  |  | 4 | R2 | 32 | 4 | 4 | ENTRANCE LOBBY | [10 empty] | 5 | [11 empty] | 1000 |  |  | RING
|  |  | 5 | Y2 | 32 | 4 | 4 | BEAUTY ROOM | [10 empty] | 4 | [12 empty] | 800 |  | RING
|  |  | 6 | B2 | 32 | 4 | 4 | MAIDROOM 1 | [10 empty] | 2 | 1 | [12 empty] | 800 | RING
| 40A 4P 30mA |  | 7 | R3 | 20 | 4 | 4 | TRADITIONAL AREA | [10 empty] | 3 | [11 empty] | 600
|  |  | 8 | Y3 | 20 | 4 | 4 | CINEMA ROOM | [10 empty] | 3 | [12 empty] | 600
|  |  | 9 | B3 | 32 | 4 | 4 | CORRIDOR + PATIO | [10 empty] | 6 | [13 empty] | 1200 | RING
|  |  | 10 | R4 | 30 | 4 | 4 | TRADITIONAL AREA | [10 empty] | 4 | [11 empty] | 800 |  |  | RING
|  |  | 11 | Y4 | 32 | 4 | 4 | CINEMA ROOM | [10 empty] | 3 | 1 | [11 empty] | 1000 |  | RING
|  |  | 12 | B4 | 20 | 4 | 4 | LAUNDRY | [10 empty] | 3 | [13 empty] | 600
| 40A 4P 30mA |  | 13 | R5 | 32 | 4 | 4 | PATIO + LOCKER | [10 empty] | 2 | 2 | [10 empty] | 1200 |  |  | RING
|  |  | 14 | Y5 | 20 | 4 | 4 | CINEMA ROOM | [10 empty] | 3 | [12 empty] | 600
|  |  | 15 | B5 | 32 | 4 | 4 | GAME ROOM | [10 empty] | 4 | 1 | [12 empty] | 1200 | RING
|  |  | 16 | R6 | 32 | 4 | 4 | PARKING | [11 empty] | 3 | [10 empty] | 1200 |  |  | RING
|  |  | 17 | Y6 | 20 | 4 | 4 | STORE | [10 empty] | 3 | [12 empty] | 600
|  |  | 18 | B6 | 32 | 4 | 4 | GAME ROOM | [11 empty] | 3 | [12 empty] | 1200 | RING ( FLOOR BOX)
| 40A 4P 30mA |  | 19 | R7 | 32 | 4 | 4 | PARKING | [10 empty] | 1 | 2 | [10 empty] | 1000 |  |  | RING
|  |  | 20 | Y7 | 20 | 4 | 4 | CINEMA ROOM | [16 empty] | 1 | [6 empty] | 1200 |  | OVEN
|  |  | 21 | B7 | 20 | 4 | 4 | GAME ROOM | [10 empty] | 3 | [13 empty] | 600
|  |  | 22 | R8 | 20 | 4 | 4 | DRIVER ROOM | [18 empty] | 1 |  |  |  | 200 |  |  | SHAVER
|  |  | 23 | Y8 | 20 | 4 | 4 | CINEMA ROOM | [15 empty] | 1 | [7 empty] | 1200 |  | MICROWAVE
|  |  | 24 | B8 | 20 | 4 | 4 | MAID ROOM BATH | [18 empty] | 1 | [5 empty] | 200 | SHAVER
| 40A 4P 30mA |  | 25 | R9 | 20 | 4 | 4 | ENTRANCE LOBBY WC | [18 empty] | 1 |  |  |  | 200 |  |  | SHAVER
|  |  | 26 | Y9 | 20 | 4 | 4 | CINEMA ROOM | [12 empty] | 1 | [10 empty] | 1000 |  | PROJECTOR
|  |  | 27 | B9 | 20 | 4 | 4 | LOCKER WC | [18 empty] | 1 | [5 empty] | 200
|  |  | 28 | R10 | 20 | 4 | 4 | TRADITIONAL AREA | [15 empty] | 1 | [6 empty] | 1200 |  |  | MICROWAVE
|  |  | 29 | Y10 | 20 | 4 | 4 | TRADITIONAL AREA | [14 empty] | 1 | [8 empty] | 500 |  | DISH WASHER
|  |  | 30 | B10 |  |  |  | SPACE | [24 empty] | 0
| 40A 4P 30mA |  | 31 | R11 | 20 | 4 | 4 | LAUNDRY | [13 empty] | 1 | [7 empty] | 500 | 500 |  |  | WASHING MACHINE
|  |  | 32 | Y11 |  |  |  | SPACE | [25 empty] | MICROWAVE
|  |  | 33 | B11 | 20 | 4 | 4 | LAUNDRY | [15 empty] | 1 | [5 empty] | 1200 |  |  | 1200
|  |  | 34 | R12 | 32 | 4 | 4 | BEAUTY ROOM | [20 empty] | 1 | 1000 | 333.3333 |  |  | 32A TP ISO
|  |  | 35 | Y12 | [27 empty] | 333.3333
|  |  | 36 | B12 | [28 empty] | 333.3333
[30 empty] | TOTAL | 8833.3333 | 8833.3333 | 8733.3333
[31 empty] | 8.8333 | 8.8333 | 8.7333
[30 empty] | TOTAL CONNECTED LOAD IN kW |  |  |  | 26.4
CABLE SIZE : 4C x 16mm2 Cu./XLPE /SWA/PVC + 1C x 16mm2 CU/PVC/ Y-G ECC. | [8 empty] | LTG = Lighting,F/O = Flex Outlet for display unit, ISO = Isolator, FCU = Fan Coil Unit
FCU = Fan Coil Unit, W/H.=Water Heater, SS/O= Socket/Outlet, DS/O = Double socket/Outlet

## DB-G-L
PROJECT: PROPOSED VILLA (B+ G+ 1) | [7 empty] | LOAD DISTRIBUTION SCHEDULE | [21 empty] | LOCATION : GROUND FLOOR
DB NOS. : DB - GF-L | [29 empty] | MOUNTING : FLUSH
FED FROM : SMDB -1 | [29 empty] | AREA |  |  | PLOT NO
RATING OF INCOMER | RATING OF ELCB |  |  |  | MCB | CCT | ECC | LOCATION | CONNECTED LOAD / POINTS | [21 empty] | LOAD PER CIRCUIT WATT |  |  | REMARKS
|  | SEC. | SL. | CIRC | RTG. | WIRE | WIRE
|  | No. | No. | No. | IN | SIZE | SIZE |  | EX-01 | EX-02 | O1 LED | SL | ML | TL | CO | CLOSET LGT | DL | CHL | T6L | 13A S/S | 13A D/S | 15A S/S | WASHING /M | MICRO/W | OVEN | COOKER | SHAVER | FCU | ISO | WATT/UNIT | R | Y | B
[5 empty] | AMP | mm2 | mm2
[9 empty] | 10 | 10 | 10 | 15 | 50 | 50 | 10 | 10 | 100 | 200 | 60 | 200 | 400 | 1000 | 500 | 1200 | 1200 | 3000 | 200
TPN ISOLATOR 40A | 40A 4P 100mA | 1 | 1 | R1 | 10 | 2.5 | 2.5 | OFFICE+OFFICE ENT + BATH |  |  |  | 18 | 1 |  | 18 | 3 | 1 | [13 empty] | 630
|  |  | 2 | Y1 | 10 | 2.5 | 2.5 | GUEST BEDRROM + BATH |  |  |  | 13 | 1 |  | 18 |  | 1 | [14 empty] | 525
|  |  | 3 | B1 | 10 | 2.5 | 2.5 | STAIR HALL |  |  | 11 | 12 |  |  | 18 | [17 empty] | 470
|  |  | 4 | R2 | 10 | 2.5 | 2.5 | KITCHEN + STORE |  |  |  | 3 |  |  | 8 | 8 |  |  | 6 | [11 empty] | 565
|  |  | 5 | Y2 | 10 | 2.5 | 2.5 | SHOW KITCHEN |  |  |  | 8 |  |  | 20 | [16 empty] | 320
|  |  | 6 | B2 | 10 | 2.5 | 2.5 | STAIR HALL | [9 empty] | 1 | [14 empty] | 200
| 40A 4P 100mA | 2 | 7 | R3 | 10 | 2.5 | 2.5 | DINNING ROOM |  |  |  | 12 |  |  | 27 | [15 empty] | 450
|  |  | 8 | Y3 | 10 | 2.5 | 2.5 | SITTING ROOM |  |  |  | 12 |  |  | 22 | [16 empty] | 400
|  |  | 9 | B3 | 10 | 2.5 | 2.5 | STAIRS |  |  | 68 | [21 empty] | 680
|  |  | 10 | R4 | 10 | 2.5 | 2.5 | DINNING ROOM | [9 empty] | 1 | [12 empty] | 200
|  |  | 11 | Y4 | 10 | 2.5 | 2.5 | SITTING ROOM | [9 empty] | 1 | [13 empty] | 200
|  |  | 12 | B4 | 10 | 2.5 | 2.5 | LIVING ROOM |  |  |  | 16 |  |  | 34 | [17 empty] | 580
| 40A 4P 100mA | 3 | 13 | R5 | 10 | 2.5 | 2.5 | DINNING ROOM | [9 empty] | 1 | [12 empty] | 200
|  |  | 14 | Y5 | 10 | 2.5 | 2.5 | POWDER ROOM + WC |  |  |  | 3 | 1 |  | 11 | 3 | 1 | [14 empty] | 335
|  |  | 15 | B5 | 10 | 2.5 | 2.5 | LIVING ROOM | [9 empty] | 1 | [14 empty] | 200
|  |  | 16 | R6 | 10 | 2.5 | 2.5 | VILLA ELEVATION | 17 |  |  | 25 | [18 empty] | 545
|  |  | 17 | Y6 | 10 | 2.5 | 2.5 | VILLA ELEVATION | 14 |  |  | 26 | [19 empty] | 530
|  |  | 18 | B6 | 10 | 2.5 | 2.5 | LIVING ROOM | [9 empty] | 1 | [14 empty] | 200
|  |  | 19 | R7 |  |  |  | SPACE | [22 empty] | 0
|  |  | 20 | Y7 |  |  |  | SPACE | [23 empty] | 0
|  |  | 21 | B7 |  |  |  | SPACE | [24 empty] | 0
|  |  | 22 | R8 | [26 empty] | 0
|  |  | 23 | Y8 | [27 empty] | 0
|  |  | 24 | B8 | [28 empty] | 0
| 40A 4P 100mA | 4 | 22 | R8 | 20 | 4 | 4 | MAIN ENTRANCE | [19 empty] | 1 |  | 200 | 200 |  |  | FCU
|  |  | 23 | Y8 | 20 | 4 | 4 | OFFICE | [19 empty] | 1 |  | 200 |  | 200 |  | FCU
|  |  | 24 | B8 | 20 | 4 | 4 | GUEST BEDRROM + BATH | [19 empty] | 1 |  | 200 |  |  | 200 | FCU
|  |  | 25 | R9 | 20 | 4 | 4 | STAIR HALL | [19 empty] | 1 |  | 200 | 200 |  |  | FCU
|  |  | 26 | Y9 | 20 | 4 | 4 | KITCHEN + STORE | [19 empty] | 1 |  | 200 |  | 200 |  | FCU
|  |  | 27 | B9 | 20 | 4 | 4 | SHOW KITCHEN | [19 empty] | 1 |  | 200 |  |  | 200 | FCU
| 40A 4P 100mA | 5 | 28 | R10 | 20 | 4 | 4 | DINNING ROOM | [19 empty] | 1 |  | 200 | 200 |  |  | FCU
|  |  | 29 | Y10 | 20 | 4 | 4 | LIVING ROOM | [19 empty] | 1 |  | 200 |  | 200 |  | FCU
|  |  | 30 | B10 | 20 | 4 | 4 | SITTING ROOM | [19 empty] | 1 |  | 200 |  |  | 2000 | FCU
|  |  | 31 | R11 | 20 | 4 | 4 | SITTING ROOM | [19 empty] | 1 |  | 200 | 200 |  |  | FCU
|  |  | 32 | Y11 |  |  |  | SPACE | [23 empty] | 0
|  |  | 33 | B11 |  |  |  | SPACE | [24 empty] | 0
|  |  | 37 | R12 | [26 empty] | 0
|  |  | 38 | Y12 | [27 empty] | 0
|  |  | 39 | B12 | [28 empty] | 0
|  |  | 40 | R13 | [26 empty] | 0
|  |  | 41 | Y13 | [27 empty] | 0
|  |  | 42 | B13 | [28 empty] | 0
|  |  | 43 | R14 | [26 empty] | 0
|  |  | 44 | Y14 | [27 empty] | 0
|  |  | 45 | B14 | [28 empty] | 0
|  |  | 46 | R15 | [26 empty] | 0
|  |  | 47 | Y15 | [27 empty] | 0
|  |  | 48 | B15 | [28 empty] | 0
[30 empty] | TOTAL | 3390 | 2910 | 4730
[31 empty] | 3.39 | 2.91 | 4.73
[30 empty] | TOTAL CONNECTED LOAD IN kW |  |  |  | 11.03
CABLE SIZE : 4C x 10mm2 Cu./XLPE /SWA/PVC + 1C x 10mm2 CU/PVC/ Y-G ECC. | [8 empty] | LTG = Lighting,F/O = Flex Outlet for display unit, ISO = Isolator, FCU = Fan Coil Unit
FCU = Fan Coil Unit, W/H.=Water Heater, SS/O= Socket/Outlet, DS/O = Double socket/Outlet

## DB-G-P
PROJECT: PROPOSED VILLA (B+ G+ 1) | [7 empty] | LOAD DISTRIBUTION SCHEDULE | [22 empty] | LOCATION : GROUND FLOOR
DB NOS. : DB - GF | [30 empty] | MOUNTING : FLUSH
FED FROM : SMDB -1 | [30 empty] | AREA |  |  | PLOT NO
RATING OF INCOMER | RATING OF ELCB |  |  |  | MCB | CCT | ECC | LOCATION | CONNECTED LOAD / POINTS | [22 empty] | LOAD PER CIRCUIT WATT |  |  | REMARKS
|  | SEC. | SL. | CIRC | RTG. | WIRE | WIRE
|  | No. | No. | No. | IN | SIZE | SIZE |  | EX-01 | EX-02 | O1 LED | SL | ML | TL | CO | CLOSET LGT | DL | CHL | T6L | 13A S/S | 13A D/S | 15A S/S | DICH WASHER | WASHING /M | MICRO/W | OVEN | COOKER | SHAVER | FCU | ISO | WATT/UNIT | R | Y | B
[5 empty] | AMP | mm2 | mm2
[9 empty] | 10 | 10 | 10 | 15 | 50 | 50 | 10 | 10 | 100 | 200 | 60 | 200 | 400 | 1000 | 500 | 500 | 1200 | 1200 | 3000 | 200
TPN ISOLATOR 63A | 40A 4P 30mA | 1 | 1 | R1 | 32 | 4 | 4 | OFFICE | [11 empty] | 4 | [10 empty] | 200 | 800 |  |  | RING
|  |  | 2 | Y1 | 32 | 4 | 4 | GUEST BEDROOM | [11 empty] | 4 | 1 | [9 empty] | 200/400 |  | 1200 |  | RING
|  |  | 3 | B1 | 20 | 4 | 4 | STAIR HALL | [11 empty] | 1 | 1 | [9 empty] | 200/400 |  |  | 600
|  |  | 4 | R2 | 32 | 4 | 4 | OFFICE | [11 empty] | 1 | 2 | [9 empty] | 200/400 | 1000 |  |  | RING
|  |  | 5 | Y2 | 32 | 4 | 4 | SHOW KITCHEN | [11 empty] | 3 | 1 | [9 empty] | 200/400 |  | 1000 |  | RING
|  |  | 6 | B2 | 32 | 4 | 4 | LIVING AREA | [11 empty] | 3 | 1 | [9 empty] | 200/400 |  |  | 1000 | RING
| 40A 4P 30mA | 2 | 7 | R3 | 32 | 4 | 4 | MAIN ENTRANCE | [11 empty] | 4 | [10 empty] | 200 | 800 |  |  | RING
|  |  | 8 | Y3 | 32 | 4 | 4 | SITTING AREA | [11 empty] | 2 | 2 | [9 empty] | 200/400 |  | 1200 |  | RING
|  |  | 9 | B3 | 32 | 4 | 4 | LIVING AREA | [12 empty] | 2 | [9 empty] | 400 |  |  | 800 | RING ( FLOOR BOX )
|  |  | 10 | R4 | 20 | 4 | 4 | KITCHEN STORE | [11 empty] | 1 | 1 | [9 empty] | 200/400 | 600
|  |  | 11 | Y4 |  |  |  | SPACE | [24 empty] | 0
|  |  | 12 | B4 | 32 | 6 | 6 | SHOW KITCHEN | [18 empty] | 1 |  |  |  | 3000 |  |  | 3000 | COOKER
| 40A 4P 30mA | 3 | 13 | R5 | 32 | 4 | 4 | KITCHEN | [11 empty] | 6 | [10 empty] | 200 | 1200 |  |  | RING
|  |  | 14 | Y5 | 20 | 4 | 4 | KITCHEN | [16 empty] | 1 | [5 empty] | 1200 |  | 1200 |  | MICROWAVE
|  |  | 15 | B5 | 20 | 4 | 4 | KITCHEN | [14 empty] | 1 | [7 empty] | 500 |  |  | 500 | DISH WASHER
|  |  | 16 | R6 | 32 | 4 | 4 | DINNING ROOM | [11 empty] | 3 | 1 | [9 empty] | 200/400 | 1000 |  |  | RING
|  |  | 17 | Y6 | 32 | 6 | 6 | KITCHEN | [18 empty] | 1 |  |  |  | 3000 |  | 3000 |  | COOKER
|  |  | 18 | B6 |  |  |  | SPACE | [25 empty] | 0
| 40A 4P 30mA | 4 | 19 | R7 | 20 | 4 | 4 | KICHEN | [17 empty] | 1 |  |  |  |  | 1200 | 1200 |  |  | OVEN
|  |  | 20 | Y7 |  |  |  | SPACE | [24 empty] | 0
|  |  | 21 | B7 |  |  |  | SPACE | [25 empty] | 0
|  |  | 22 | R8 | [27 empty] | 0
|  |  | 23 | Y8 | [28 empty] | 0
|  |  | 24 | B8 | [29 empty] | 0
|  |  | 25 | R8 | 20 | 4 | 4 | OFFICE BATH | [19 empty] | 1 |  |  | 200 | 200 |  |  | SHAVER
|  |  | 26 | Y8 | 20 | 4 | 4 | GUEST BATH | [19 empty] | 1 |  |  | 200 |  | 200 |  | SHAVER
|  |  | 27 | B8 | 20 | 4 | 4 | POWDER ROOM | [19 empty] | 1 |  |  | 200 |  |  | 200 | SHAVER
|  |  | 28 | R9 |  |  |  | SPACE | [23 empty] | 0
|  |  | 29 | Y9 |  |  |  | SPACE | [24 empty] | 0
|  |  | 30 | B9 |  |  |  | SPACE | [25 empty] | 0
|  |  | 31 | R10 | [27 empty] | 0
|  |  | 32 | Y10 | [28 empty] | 0
|  |  | 33 | B10 | [29 empty] | 0
|  |  | 34 | R11 | [27 empty] | 0
|  |  | 35 | Y11 | [28 empty] | 0
|  |  | 36 | B11 | [29 empty] | 0
|  |  | 37 | R12 | [27 empty] | 0
|  |  | 38 | Y12 | [28 empty] | 0
|  |  | 39 | B12 | [29 empty] | 0
|  |  | 40 | R13 | [27 empty] | 0
|  |  | 41 | Y13 | [28 empty] | 0
|  |  | 42 | B13 | [29 empty] | 0
|  |  | 43 | R14 | [27 empty] | 0
|  |  | 44 | Y14 | [28 empty] | 0
|  |  | 45 | B14 | [29 empty] | 0
|  |  | 46 | R15 | [27 empty] | 0
|  |  | 47 | Y15 | [28 empty] | 0
|  |  | 48 | B15 | [29 empty] | 0
[31 empty] | TOTAL | 6800 | 7800 | 6100
[32 empty] | 6.8 | 7.8 | 6.1
[31 empty] | TOTAL CONNECTED LOAD IN kW |  |  |  | 20.7
CABLE SIZE : 4C x 16mm2 Cu./XLPE /SWA/PVC + 1C x 16mm2 CU/PVC/ Y-G ECC. | [8 empty] | LTG = Lighting,F/O = Flex Outlet for display unit, ISO = Isolator, FCU = Fan Coil Unit
FCU = Fan Coil Unit, W/H.=Water Heater, SS/O= Socket/Outlet, DS/O = Double socket/Outlet

## DB-F-L
PROJECT: PROPOSED VILLA (B+ G+ 1) | [7 empty] | LOAD DISTRIBUTION SCHEDULE | [21 empty] | LOCATION : FIRST FLOOR
DB NOS. : DB - F-L | [29 empty] | MOUNTING : FLUSH
FED FROM : SMDB -1 | [29 empty] | AREA |  |  | PLOT NO
RATING OF INCOMER | RATING OF ELCB |  |  |  | MCB | CCT | ECC | LOCATION | CONNECTED LOAD / POINTS | [21 empty] | LOAD PER CIRCUIT WATT |  |  | REMARKS
|  | SEC. | SL. | CIRC | RTG. | WIRE | WIRE
|  | No. | No. | No. | IN | SIZE | SIZE |  | EX-01 | EX-02 | O1 LED | SL | ML | TL | CO | CLOSET LGT | DL | CHL | T6L | 13A S/S | 13A D/S | 15A S/S | WASHING /M | MICRO/W | OVEN | COOKER | SHAVER | FCU | ISO | WATT/UNIT | R | Y | B
[5 empty] | AMP | mm2 | mm2
[9 empty] | 10 | 10 | 10 | 15 | 50 | 50 | 10 | 10 | 100 | 200 | 60 | 200 | 400 | 1000 | 500 | 1200 | 1200 | 3000 | 200
TPN ISOLATOR 40A | 40A 4P 100mA | 1 | 1 | R1 | 10 | 2.5 | 2.5 | BEDROOM 1 | 2 |  |  | 12 |  |  | 18 |  | 1 | [13 empty] | 480
|  |  | 2 | Y1 | 10 | 2.5 | 2.5 | BEDROOM 2 | 2 |  |  | 12 |  |  | 22 |  | 1 | [14 empty] | 520
|  |  | 3 | B1 | 10 | 2.5 | 2.5 | BEDROOM 3 | 2 |  |  | 12 |  |  | 28 |  | 1 | [15 empty] | 580
|  |  | 4 | R2 | 10 | 2.5 | 2.5 | CLOSET 1 + BATH 1 |  |  | 8 | 3 | 1 |  | 16 | 11 | 1 | [13 empty] | 545
|  |  | 5 | Y2 | 10 | 2.5 | 2.5 | CLOSET 2 + BATH 2 |  |  |  | 3 | 1 |  | 12 | 5 | 1 | [14 empty] | 365
|  |  | 6 | B2 | 10 | 2.5 | 2.5 | CLOSET 3 + BATH 3 |  |  | 8 | 7 | 1 |  | 14 | 10 | 1 | [15 empty] | 575
| 40A 4P 100mA | 2 | 7 | R3 | 10 | 2.5 | 2.5 | BEDROOM 4 | 2 |  |  | 12 |  |  | 24 |  | 1 | [13 empty] | 540
|  |  | 8 | Y3 | 10 | 2.5 | 2.5 | MASTER BEDROOM | 2 |  |  | 8 |  |  | 28 |  | 1 | [14 empty] | 520
|  |  | 9 | B3 | 10 | 2.5 | 2.5 | MAIN ENTRANCE |  |  |  | 8 |  |  | 10 | [17 empty] | 220
|  |  | 10 | R4 | 10 | 2.5 | 2.5 | CLOSET 4 + BATH 4 |  |  | 5 | 6 | 1 |  | 8 | 6 | 1 | [13 empty] | 430
|  |  | 11 | Y4 | 10 | 2.5 | 2.5 | MASTER CLOSET + BATH + SAFE BOX |  |  |  | 23 | 2 |  | 25 | 21 | 2 | [14 empty] | 1105
|  |  | 12 | B4 | 10 | 2.5 | 2.5 | MAIN ENTRANCE | [9 empty] | 1 | [14 empty] | 200
| 40A 4P 100mA | 3 | 13 | R5 | 10 | 2.5 | 2.5 | VOID - MAIN ENTRANCE |  |  |  | 12 |  |  | 18 | [15 empty] | 360
|  |  | 14 | Y5 | 10 | 2.5 | 2.5 | STAIR HALL | [9 empty] | 1 | [13 empty] | 200
|  |  | 15 | B5 | 10 | 2.5 | 2.5 | STAIR HALL VOID | [9 empty] | 1 | [14 empty] | 200
|  |  | 16 | R6 | 10 | 2.5 | 2.5 | VOID - MAIN ENTRANCE | [9 empty] | 1 | [12 empty] | 200
|  |  | 17 | Y6 | 10 | 2.5 | 2.5 | STAIR HALL |  |  |  | 12 |  |  | 22 | [16 empty] | 400
|  |  | 18 | B6 | 10 | 2.5 | 2.5 | STAIR |  |  | 44 | 3 | [20 empty] | 485
| 40A 4P 100mA | 4 | 19 | R7 | 10 | 2.5 | 2.5 | PANTRY + LAUNDRY | [10 empty] | 8 | [11 empty] | 480
|  |  | 20 | Y7 | 10 | 2.5 | 2.5 | PRIVATE HALL |  |  |  | 8 |  |  | 14 |  | 1 | [14 empty] | 360
|  |  | 21 | B7 | 10 | 2.5 | 2.5 | BACK ENTRANCE |  |  |  | 8 | [20 empty] | 120
|  |  | 22 | R8 | 10 | 2.5 | 2.5 | ROOF | 16 | [21 empty] | 160
|  |  | 23 | Y8 | 10 | 2.5 | 2.5 | SERVICE ROOM | [5 empty] | 18 | [17 empty] | 900
|  |  | 24 | B8 | 10 | 2.5 | 2.5 | BACK ENTRANCE | [6 empty] | 16 |  |  | 1 | [14 empty] | 360
|  |  | 25 | R9 | 10 | 2.5 | 2.5 | ROOF ( STORE ) | [5 empty] | 5 | [16 empty] | 250
|  |  | 26 | Y9 |  |  |  | SPACE | [23 empty] | 0
|  |  | 27 | B9 |  |  |  | SPACE | [24 empty] | 0
|  |  | 28 | R10 | [26 empty] | 0
|  |  | 29 | Y10 | [27 empty] | 0
|  |  | 30 | B10 | [28 empty] | 0
| 40A 4P 100mA | 5 | 31 | R10 | 20 | 4 | 4 | BEDROOM 1 | [19 empty] | 1 |  | 200 | 200
|  |  | 32 | Y10 | 20 | 4 | 4 | BEDROOM 2 | [19 empty] | 1 |  | 200 |  | 200
|  |  | 33 | B10 | 20 | 4 | 4 | STAIR HALL | [19 empty] | 1 |  | 200 |  |  | 200
|  |  | 34 | R11 | 20 | 4 | 4 | PRIVATE HALL | [19 empty] | 1 |  | 200 | 200
|  |  | 35 | Y11 | 20 | 4 | 4 | LAUNDRY | [19 empty] | 1 |  | 200 |  | 200
|  |  | 36 | B11 | 20 | 4 | 4 | BEDROOM 3 | [19 empty] | 1 |  | 200 |  |  | 200
| 40A 4P 100mA | 6 | 37 | R12 | 20 | 4 | 4 | BEDROOM 4 | [19 empty] | 1 |  | 200 | 200
|  |  | 38 | Y12 | 20 | 4 | 4 | MASTER BEDROOM | [19 empty] | 1 |  | 200 |  | 200
|  |  | 39 | B12 |  |  |  | SPACE | [24 empty] | 0
|  |  | 40 | R13 |  |  |  | SPACE | [22 empty] | 0
|  |  | 41 | Y13 |  |  |  | SPACE | [23 empty] | 0
|  |  | 42 | B13 |  |  |  | SPACE | [24 empty] | 0
| 40A 4P 30mA | 7 | 43 | R14 | [26 empty] | 0
|  |  | 44 | Y14 | [27 empty] | 0
|  |  | 45 | B14 | [28 empty] | 0
|  |  | 46 | R15 | [26 empty] | 0
|  |  | 47 | Y15 | [27 empty] | 0
|  |  | 48 | B15 | [28 empty] | 0
[30 empty] | TOTAL | 4045 | 4970 | 3140
[31 empty] | 4.045 | 4.97 | 3.14
[30 empty] | TOTAL CONNECTED LOAD IN kW |  |  |  | 12.155
CABLE SIZE : 4C x 25mm2 Cu./XLPE /SWA/PVC + 1C x 16mm2 CU/PVC/ Y-G ECC. | [8 empty] | LTG = Lighting,F/O = Flex Outlet for display unit, ISO = Isolator, FCU = Fan Coil Unit
FCU = Fan Coil Unit, W/H.=Water Heater, SS/O= Socket/Outlet, DS/O = Double socket/Outlet

## DB-F-P
PROJECT: PROPOSED VILLA (B+ G+ 1) | [7 empty] | LOAD DISTRIBUTION SCHEDULE | [21 empty] | LOCATION : FIRST FLOOR
DB NOS. : DB - F-L | [29 empty] | MOUNTING : FLUSH
FED FROM : SMDB -1 | [29 empty] | AREA |  |  | PLOT NO
RATING OF INCOMER | RATING OF ELCB |  |  |  | MCB | CCT | ECC | LOCATION | CONNECTED LOAD / POINTS | [21 empty] | LOAD PER CIRCUIT WATT |  |  | REMARKS
|  | SEC. | SL. | CIRC | RTG. | WIRE | WIRE
|  | No. | No. | No. | IN | SIZE | SIZE |  | EX-01 | EX-02 | O1 LED | SL | ML | TL | CO | CLOSET LGT | DL | CHL | T6L | 13A S/S | 13A D/S | 15A S/S | WASHING /M | MICRO/W | OVEN | COOKER | SHAVER | FCU | ISO | WATT/UNIT | R | Y | B
[5 empty] | AMP | mm2 | mm2
[9 empty] | 10 | 10 | 10 | 15 | 50 | 50 | 10 | 10 | 100 | 200 | 60 | 200 | 400 | 1000 | 500 | 1200 | 1200 | 3000 | 200
TPN ISOLATOR 40A | 40A 4P 30mA | 1 | 1 | R1 | 32 | 4 | 4 | BEDROOM 1 | [11 empty] | 4 | 1 | [9 empty] | 1200 |  |  | RING
|  |  | 2 | Y1 | 32 | 4 | 4 | BEDROOM 2 | [11 empty] | 4 | 1 | [10 empty] | 1200 |  | RING
|  |  | 3 | B1 | 32 | 4 | 4 | BEDROOM 3 | [11 empty] | 4 | 1 | [11 empty] | 1200 | RING
|  |  | 4 | R2 | 20 | 4 | 4 | CLOSET 1 | [11 empty] | 3 | [10 empty] | 600
|  |  | 5 | Y2 | 20 | 4 | 4 | CLOSET 2 | [11 empty] | 2 | [11 empty] | 400
|  |  | 6 | B2 | 32 | 4 | 4 | BEDROOM 3 + CLOSET 3 | [11 empty] | 2 | 1 | [11 empty] | 800 | RING
| 40A 4P 30mA | 2 | 7 | R3 | 32 | 4 | 4 | BEDROOM 4 | [11 empty] | 4 | [10 empty] | 800 |  |  | RING
|  |  | 8 | Y3 | 32 | 6 | 6 | MASTER BEDROOM | [11 empty] | 6 | [11 empty] | 1200 |  | RING
|  |  | 9 | B3 | 32 | 4 | 4 | STAIR HALL | [12 empty] | 2 | [11 empty] | 800 | RING ( FLOOR BOX)
|  |  | 10 | R4 | 32 | 4 | 4 | BEDROOM 4 + CLOSET | [11 empty] | 3 | 1 | [9 empty] | 1000 |  |  | RING
|  |  | 11 | Y4 | 32 | 4 | 4 | MASTER BEDRROOM + CLOSET | [11 empty] | 4 | 1 | [10 empty] | 1200 |  | RING
|  |  | 12 | B4 |  |  |  | SPACE | [24 empty] | 0
| 40A 4P 30mA | 3 | 13 | R5 | 32 | 4 | 4 | PANTRY | [11 empty] | 5 | [10 empty] | 1000 |  |  | RING
|  |  | 14 | Y5 | 32 | 4 | 4 | SAFE BOX | [11 empty] | 2 | 1 | [10 empty] | 800 |  | RING
|  |  | 15 | B5 | 32 | 6 | 6 | PANTRY | [17 empty] | 1 |  |  |  | 3000 |  |  | 3000 | COOKER
|  |  | 16 | R6 | 20 | 4 | 4 | PANTRY | [15 empty] | 1 | [5 empty] | 1200 | 1200 |  |  | MICROWAVE
|  |  | 17 | Y6 | 32 | 4 | 4 | STAIR HALL | [11 empty] | 3 | 1 | [10 empty] | 1000 |  | RING
|  |  | 18 | B6 | 32 | 4 | 4 | ROOF | [11 empty] | 5 | [12 empty] | 1000 | RING
| 40A 4P 30mA | 4 | 19 | R7 | 20 | 4 | 4 | BEDROOM 1 | [18 empty] | 1 |  |  |  | 200 |  |  | SHAVER
|  |  | 20 | Y7 | 20 | 4 | 4 | BEDRROM 2 | [18 empty] | 1 |  |  |  |  | 200 |  | SHAVER
|  |  | 21 | B7 | 20 | 4 | 4 | BEDROOM 3 | [18 empty] | 1 | [5 empty] | 200 | SHAVER
|  |  | 22 | R8 | 20 | 4 | 4 | BEDROOM 4 | [18 empty] | 1 |  |  |  | 200 |  |  | SHAVER
|  |  | 23 | Y8 | 20 | 4 | 4 | BEDROOM 5 | [18 empty] | 1 |  |  |  |  | 200 |  | SHAVER
|  |  | 24 | B8 | [28 empty] | 0
| 40A 4P 30mA | 5 | 25 | R9 | [26 empty] | 0
|  |  | 26 | Y9 | [27 empty] | 0
|  |  | 27 | B9 | [28 empty] | 0
|  |  | 28 | R10 | [26 empty] | 0
|  |  | 29 | Y10 | [27 empty] | 0
|  |  | 30 | B10 | [28 empty] | 0
|  |  | 31 | R10
|  |  | 32 | Y10
|  |  | 33 | B10
|  |  | 34 | R11
|  |  | 35 | Y11
|  |  | 36 | B11
|  |  | 37 | R12
|  |  | 38 | Y12
|  |  | 39 | B12 | [28 empty] | 0
|  |  | 40 | R13 | [26 empty] | 0
|  |  | 41 | Y13 | [27 empty] | 0
|  |  | 42 | B13 | [28 empty] | 0
|  |  | 43 | R14 | [26 empty] | 0
|  |  | 44 | Y14 | [27 empty] | 0
|  |  | 45 | B14 | [28 empty] | 0
|  |  | 46 | R15 | [26 empty] | 0
|  |  | 47 | Y15 | [27 empty] | 0
|  |  | 48 | B15 | [28 empty] | 0
[30 empty] | TOTAL | 6200 | 6200 | 7000
[31 empty] | 6.2 | 6.2 | 7
[30 empty] | TOTAL CONNECTED LOAD IN kW |  |  |  | 19.4
CABLE SIZE : 4C x 10mm2 Cu./XLPE /SWA/PVC + 1C x 10mm2 CU/PVC/ Y-G ECC. | [8 empty] | LTG = Lighting,F/O = Flex Outlet for display unit, ISO = Isolator, FCU = Fan Coil Unit
FCU = Fan Coil Unit, W/H.=Water Heater, SS/O= Socket/Outlet, DS/O = Double socket/Outlet

## SMDB-RF
PROJECT: PROPOSED RESIDENCE VILLA B+G+1+R | [5 empty] | DETAILS OF CONNECTED LOAD/MAX. DEMAND | [8 empty] | LOCATION : ROOF
[6 empty] | OWNER : MR.HASSAN KHALES SAKANDASTGIR | [8 empty] | AREA : AL THANYAH FOURTH
SMDB-R | [14 empty] | PLOT NO : 3940198
FED FROM : SEWA | [5 empty] | CONSULTANT:
CIRCUIT / |  | TP/ SP | RATING - AMPS |  |  | FAULT DUTY kA | PVC / | CABLE SIZE |  | ECC | CONNECTED LOAD - Kw |  |  |  | PROPOSED TYPE & NO. OF |  |  |  | REMARKS
FEEDER | [6 empty] | XLPE |  |  | SIZE |  |  |  |  | Kwh METERS
DB NO. |  |  | F/S ISO | MCCB ACB | MCB |  | SWA / | 2 / 4 X | 2 / 3 / 4C | 1C | R - PH | Y - PH | B - PH | TOTAL | 1 - PH | 3 - PH | 3 - PH | LV /HV
[7 empty] | PVC | 1C MM2 | MM2 | mm2 | kW | kW | kW | kW | -1 | -2 | -3 | CT (4)
| INCOMER | TP |  | 200 |  | 35 | XLPE |  | 4CX95 | 1CX50 | 24.3333 | 26.3333 | 28.7333 | 79.4
OUT GOING :
1 | FAHU | TP |  | 63 |  | 25 | XLPE |  | 4CX16 | 1CX16 | 6 | 6 | 6 | 18 |  |  |  |  | 100mA ELCB
2 | ODU - 1 | TP |  | 63 |  | 25 | XLPE |  | 4CX16 | 1CX16 | 3.3333 | 3.3333 | 3.3333 | 10 |  |  |  |  | 100mA ELCB
3 | VRV 1A | TP |  | 40 |  | 25 | XLPE |  | 4CX10 | 1CX10 | 2.5 | 2.5 | 2.5 | 7.5 |  |  |  |  | 100mA ELCB
4 | VRV 1B | TP |  | 40 |  | 25 | XLPE |  | 4CX10 | 1CX10 | 2.5 | 2.5 | 2.5 | 7.5 |  |  |  |  | 300mA ELCB
5 | VRV G-A | TP |  | 40 |  | 25 | XLPE |  | 4CX10 | 1CX10 | 2.5 | 2.5 | 2.5 | 7.5 |  |  |  |  | 100mA ELCB
6 | VRV G-B | TP |  | 40 |  | 25 | XLPE |  | 4CX10 | 1CX10 | 2.5 | 2.5 | 2.5 | 7.5 |  |  |  |  | 30mA ELCB
7 | VRV B-A | TP |  | 40 |  | 25 | XLPE |  | 4CX10 | 1CX10 | 2.5 | 2.5 | 2.5 | 7.5 |  |  |  |  | 30mA ELCB
8 | VRV B-B | TP |  | 40 |  | 25 | XLPE |  | 4CX10 | 1CX10 | 2.5 | 2.5 | 2.5 | 7.5 |  |  |  |  | 100mA ELCB
9 | SOLAR HEATER 1 | SP |  | 40 |  | 25 | XLPE |  | 2CX6 | 1CX6 |  |  | 2 | 2 |  |  |  |  | 100mA ELCB
10 | SOLAR HEATER 2 | SP |  | 40 |  | 25 | XLPE |  | 2CX6 | 1CX6 |  | 2 |  | 2 |  |  |  |  | 100mA ELCB
11 | CIRCULATION PUMP | SP |  | 40 |  | 25 | XLPE |  | 2CX4 | 1CX4 |  |  | 0.2 | 0.2 |  |  |  |  | 100mA ELCB
12 | TRANSFEER PUMP | SP |  | 40 |  | 25 | XLPE |  | 2CX6 | 1CX6 |  |  | 2.2 | 2.2
[6 empty] | TOTAL CONNECTION LOAD PER PHASE |  |  |  |  | 24.3333 | 26.3333 | 28.7333 | 79.4 |  |  |  | 1 | TOTAL
| MAX.DEMAND (3PH) : | 67.49 | kW AT 0.850 DIVERSITY |  |  |  |  | TOTAL CONNECTED LOAD (3PH) : |  |  |  |  | 79.4 | kW | = | 99.25 |  | kVA
| CONTRACTOR :...................................................................................... | [9 empty] | TEL: .............................................................. |  |  |  |  | FAX: ................................................
| Type of Meter (Rating of Incomer) |  |  |  |  | (2) UP to 60 A |  |  | (2) UP to 100 A |  | (3) 125 - 160 A |  |  | (4) LV CT ........../ .........A / HV CT .........../.........A
[6 empty] | (1 Phase) |  |  | (3 Phase)

## MDB
PROJECT: PROPOSED RESIDENCE VILLA B+G+1+R
PROJECT NO: 3940198 | [7 empty] | DETAILS OF CONNECTED LOAD / MAX. DEMAND | [6 empty] | AREA :AL THANYAH FOURTH, DUBAI
PANEL : MDB | [7 empty] | OWNER : MR.HASSAN KHALES SAKANDASTGIR
FED FROM : DEWA | [14 empty] | LOCATION OF MDB: SERVICE ROOM
CIRCUIT |  |  |  | RATING AMPS |  | FAULT DUTY | PVC | CABLE SIZE |  | ECC |  | CONNECTED LOAD KWH |  | T.C.L OF | PROPOSED KWH METER
FEEDER | SP | TP | F/S ISOL | MCCB | ELCB |  | XLPE | 2/4X1C | 2/3/4C | SIZE | R.PH | Y.PH | B.PH | EACH DB | 1. 1PH | 2. 3PH | 3. 3PH | 4. CT | REMARKS
INCOMER |  | TP |  | 400 |  | 35kA | XLPE |  | 4C X300 | 1C 150 | 75.1267 | 74.1667 | 75.8067 | 225.1 |  |  |  | 1 | 400/5A CT
OUTGOING
DB-EXT |  | TP |  | 40 |  | 25kA | XLPE/SWA/PVC |  | 4C 10 | 1C 10 | 7.13 | 4.46 | 3.64 | 15.23
DB-UGF-L |  | TP |  | 40 |  | 25kA | XLPE/SWA/PVC |  | 4C 10 | 1C 10 | 3.395 | 1.66 | 2.73 | 7.785
DB-UGF-P |  | TP |  | 63 |  | 25KA | XLPE/SWA/PVC |  | 4C 16 | 1C 16 | 8.8333 | 8.8333 | 8.7333 | 26.4
DB-G-L |  | TP |  | 40 |  | 25KA | XLPE/SWA/PVC |  | 4C 10 | 1C 10 | 3.39 | 2.91 | 4.73 | 11.03
DB-G-P |  | TP |  | 63 |  | 25kA | XLPE/SWA/PVC |  | 4C 16 | 1C 16 | 6.8 | 7.8 | 6.1 | 20.7
DB-F-L |  | TP |  | 40 |  | 25kA | XLPE/SWA/PVC |  | 4C 10 | 1C 10 | 4.045 | 4.97 | 3.14 | 12.155
DB-F-P |  | TP |  | 40 |  | 25kA | XLPE/SWA/PVC |  | 4C 10 | 4C 10 | 6.2 | 6.2 | 7 | 19.4
SMDB-RF |  | TP |  | 250 |  | 25kA | XLPE/SWA/PVC |  | 4C 150 | 1C 70 | 24.3333 | 26.3333 | 28.7333 | 79.4
SWIMMING POOL PANEL |  | TP |  | 63 |  | 25kA | XLPE/SWA/PVC |  | 4C 16 | 1C 16 | 5 | 5 | 5 | 15 |  |  |  |  | 100mA ELCB
LIFT |  | TP |  | 40 |  | 25kA | XLPE/SWA/PVC |  | 4C 10 | 1C 10 | 2 | 2 | 2 | 6 |  |  |  |  | 300mA ELCB
CAR CHARGER 1 |  | TP |  | 40 |  | 25kA | XLPE/SWA/PVC |  | 4C 10 | 1C 10 | 2 | 2 | 2 | 6 |  |  |  |  | 100mA ELCB
CAR CHARGER 2 |  | TP |  | 40 |  | 25kA | XLPE/SWA/PVC |  | 4C 10 | 4C 10 | 2 | 2 | 2 | 6 |  |  |  |  | 100mA ELCB
[11 empty] | 75.1267 | 74.1667 | 75.8067 | 225.1
MAX DEMAND (3PH) |  |  | 202.59 |  | kW | 90% DIVERSITY |  | TOTAL CONNECTED LOAD (3PH) : |  |  |  |  | 225.1 | kW
PROVIDED CT - METER WHEN MAX. DEMAND >100KW
[11 empty] | (1) 20-80A |  | (2) 30-90/120A |  | (3) 100-200A |  | (4)…./….A